## ReadOnly Bits
Scadaflex II Communication Register List
Modbus Input Points | DF1 Bank 3 | Description
1 | 1 | Local DI's
13 | 13 | Pulse Inputs
5001 | 17 | Remote Sensor Status Bits ( 8 * 64 )
5513 | 529 | Com Fail Status
5521 | 537 | Destination ComFail
5553 | 569 | Pump Outputs
5556 | 572 | Pump Error
5557 | 573 | Log Run Indicator
5558 | 574 | Basic First Scan
5559 | 575 | Basic Run Indicator
5560 | 576 | Alarm Active (ALL groups)
5561 | 577 | Alarm Active (per group)
5569 | 585 | DO Relay State
5573 | 589 | Local Force Enables
5577 | 593 | Alarm Bits
6337 | 1353 | FTP Error
6338 | 1354 | Lockout

## Bits
Scadaflex II Communication Register List
Modbus Coils | DF1 Bank 13 | Description
1 | 1 | DO (1-4)
1001 | 101 | B Registers ( 1 - 504)
5001 |  | Alarm Acknowledge Bits
5761 |  | Com Stats Clear
5762 |  | DI Totalizer Clear
5764 |  | Pump Run Starts Clear
5766 |  | Ethernet Master Comm Trigger
5767 |  | Serial Master Comm Trigger
5768 |  | Cell Master Comm Trigger
5769 |  | Event Trigger (1-32)
5801 |  | Command Triggers (1-16)
5817 |  | DO Force Enable
5825 |  | DO Force Value
5833 |  | DI Force Enable
5849 |  | DI Force Value
5865 |  | AI Force Enable
5873 |  | AO Force Enable
5881 |  | DI Invert
5897 |  | Set DO on Comm Fail - DO 01
5905 |  | ComFail DO Value
5913 |  | Digital Test Mode Enable
5914 |  | Disable WAN HTTP Config Service
5915 |  | Show Forcing on Local IO Page
5916 |  | TFTP Enable
5917 |  | Ethernet Master Use Retries on Probing
5918 |  | Serial Master Use Retries on Probing
5919 |  | Cell Master Use Retries on Probing
5920 |  | Slow Trending ( Trend every 8 seconds)
5921 |  | Enable VPII Buzzer on Alarm
5922 |  | External HMI Force Enable
5923 |  | Remote HMI - Enable Buttons
5924 |  | Remote HMI - Enable Setpoint edit
5925 |  | Use DHCP
5926 |  | Allow Unsecured WUI Read Only Access
5927 |  | Low Power Enable
5928 |  | Trace - Strip Mode Enabled
5929 |  | Temp C / F
5930 |  | Use Local time in Trend files
5931 |  | Daylight Savings Time Enable
5932 |  | Allow off Schedule Acks
5933 |  | Include Acked Alarms in Messages
5934 |  | Show Idle Alarms on Website
5935 |  | Enable the All I Page
5936 |  | Enable the All B Page
5937 |  | Write Enable the All I Page
5938 |  | Write Enable the All B Page
5939 |  | Show kPa in ##.# format
5940 |  | Ethernet Auto PowerDown
5941 |  | European Mode Enable
5942 |  | PID 1 Reverse Acting
5943 |  | PID 2 Reverse Acting
5944 |  | Alive Message - Skip if Alarmed in last 24 hours
5945 |  | Display Underscore as Space
5946 |  | Ethernet: Use HTTP Accelerator
5947 |  | CellData: Use HTTP Accelerator
5948 |  | WEB Debug Enable
5949 |  | Enable Command Cell Logging
5950 |  | Enable SDX Cell Logging
5951 |  | Text Message Interface "?" - Vin Enable
5952 |  | Text Message Interface "?" - Cell RSSI Enable
5953 |  | Report on Cleared Alarms
5954 |  | Add Alarms to Cleared Report
5955 |  | Analog Test Mode Enable
5956 |  | Only except SMS/ Email Messages from Known Contacts
5957 |  | Log Diagnostics to Event Log
5958 |  | Enable Debug Mode
5959 |  | On Pump Fail Leave Call On
5960 |  | FTP Use CellData
5961 |  | Create Error/Journal Logs Oldest to Newest
5962 |  | Adjust Rcvd Message TimeStamp for DST
5963 |  | SMTP Use AUTH
5964 |  | Notification Trigger
5965 |  | FTP Trigger
5966 |  | Do Not Parse "rpt" files
5967 |  | Switch Test
5968 |  | Include Template Report
5969 |  | SMS Notify include Page 0 (Home)
5970 |  | SMS Notify include Page 1
5971 |  | SMS Notify include Page 2
5972 |  | SMS Notify include Page 3
5973 |  | SMS Notify include Page 4
5974 |  | FTP Error Log
5975 |  | FTP Event Log
5976 |  | FTP Journal
5977 |  | AO ComFail Enables
5979 |  | FTP Preface file name with unit Name
5985 |  | Ethernet Port SDX Enable
5986 |  | Ethernet Port Modbus Enable
5991 |  | Ethernet VPII Enable
5993 |  | Serial Port SDX Enable
5994 |  | Serial Port Modbus Enable
5995 |  | Serial Port DF1 Enable
6001 |  | Cell Port SDX Enable
6002 |  | Cell Port Modbus Enable
6005 |  | Texting Mode Enable
6006 |  | Cell Port STM Enable
6009 |  | Display Item on ? ConcentratorDI's
6025 |  | Display Item on ? Concentrator DO's
6033 |  | Display Item on ? Concentrator AI's
6041 |  | Display Item on ? Concentrator AO's
6049 |  | Display Item on ? Concentrator B's
6553 |  | Display Item on ? Concentrator I's
7057 |  | Concentrator I Retain Enable's
7185 |  | Concentrator B Retain Enable's
7249 |  | Include HMI Item in LCD scan mode
7305 |  | Logging Attach to Right Axis Trace 1-64
7369 |  | Master Engine Destination Disable
7401 |  | ScaleBlock Unsignd/Signed Selector 1-32
7433 |  | Disable 'Full Website' on Mobile
7434 |  | Disable 'Trend' on Mobile
7435 |  | Disable 'Alarms' on Mobile
7436 |  | Enable 'Graphic HMI' on Mobile
7441 |  | Concentrator Bit Write Enable B's
7945 |  | Concentrator Integer Write Enable I's
8449 |  | Display Item on WEB Concentrator B's
8953 |  | Display Item on WEB Concentrator I's
9457 |  | Display Item on WEB User Commands
9473 |  | Site CheckIn Alarm Group Enable (1-8)
9481 |  | Status Alert Alarm Group Enable (1-8)
9489 |  | Remote Sensor Mode [Bit 0]
9490 |  | Remote Sensor Mode [Bit 1]
9491 |  | Remote Sensor Mode [Bit 2]
9493 |  | Remote Sensor DI OnChange Enable
9494 |  | Remote Sensor PI Enable (DI4)
9495 |  | DO1 Pulse Enable
9496 |  | DO2 Pulse Enable
9497 |  | Remote Sensor Cfg Block (2-64)

## Read Only Integers
Scadaflex II Communication Register List
Modbus Input Registers | DF1 Bank 7 | Description
1 | 1 | AI Registers
5 | 5 | Internal Temperature
6 | 6 | VIN ( x100mV)
7 | 7 | VBATT ( x100mV)
5001 | 8 | PI Rate (1 & 2)
5003 | 10 | PI Interval (1 & 2) [ 2 x 32 Bit]
5007 | 14 | Ethernet Slave TX/RX Packets [ 2 x 32 Bit]
5011 | 18 | Serial Slave TX/RX Packets [ 2 x 32 Bit]
5015 | 22 | Cell Slave TX/RX Packets [ 2 x 32 Bit]
5019 | 26 | XBee Slave TX/RX Packets [ 2 x 32 Bit]
5023 | 30 | Master Destination TX/RX Packets [ 2 x 32 Bit] (1-32)
5151 | 158 | Current Cell Data TX/RX Bytes [ 2 x 32 Bit]
5155 | 162 | Last Month Cell Data TX/RX Bytes [ 2 x 32 Bit]
5159 | 166 | Current Month Cell SMS TX/RX Bytes [ 2 x 32 Bit]
5163 | 170 | Last Month Cell SMS TX/RX Bytes [ 2 x 32 Bit]
5167 | 174 | Master Success - Ethernet %
5168 | 175 | Master Success - Serial %
5169 | 176 | Master Success - Cell Port %
5170 | 177 | Cell phone Signal Strength (RSSI)
5171 | 178 | VIN ( x100mV)
5172 | 179 | Last SDX Error Code
5173 | 180 | Last Error Extension
5174 | 181 | Last Source Address - Ethernet
5175 | 182 | Last Source Address - Serial
5176 | 183 | Last Source Address - Cell
5177 | 184 | Last Destination Address - Ethernet
5178 | 185 | Last Destination Address - Serial
5179 | 186 | Last Destination Address - Cell
5180 | 187 | Last Source Address for us - Ethernet
5181 | 188 | Last Source Address for us - Serial
5182 | 189 | Last Source Address for us - Cell
5183 | 190 | Destination Com Fail Counts (1-32)
5215 | 222 | Ethernet Com Fail Counts
5216 | 223 | Serial Com Fail Counts
5217 | 224 | Cell Com Fail Counts
5218 | 225 | XBee Com Fail Counts
5219 | 226 | Ethenet Slave Latency Live
5220 | 227 | Ethenet Slave Latency Last
5221 | 228 | Ethenet Slave Latency Max
5222 | 229 | Serial Slave Latency Live
5223 | 230 | Serial Slave Latency Last
5224 | 231 | Serial Slave Latency Max
5225 | 232 | Cell Slave Latency Live
5226 | 233 | Cell Slave Latency Last
5227 | 234 | Cell Slave Latency Max
5228 | 235 | XBee Slave Latency Live
5229 | 236 | XBee Slave Latency Last
5230 | 237 | XBee Slave Latency Max
5231 | 238 | Destination Latency Last (1-32)
5263 | 270 | Systick [32 bit]
5265 | 272 | Programming Scan Time
5266 | 273 | Programming Scan Time MAX
5267 | 274 | Programming Error Code
5268 | 275 | Programming Error Line
5269 | 276 | RS Error
5270 | 277 | Journal Stats (% used)
5271 | 278 | Event Log Stats (% used)
5272 | 279 | Error Log Stats (% used)
5273 | 280 | PID Error (1 & 2 )
5275 | 282 | PID Output (1 & 2 )
5277 | 284 | PID DeadBand Output (1 & 2 )
5279 | 286 | PID P Out [32 Bit] (1 & 2 )
5283 | 290 | PID I Out [32 Bit] (1 & 2 )
5283 | 290 | PID D Out [32 Bit] (1 & 2 )
5287 | 294 | CellData Debug Stats

## Integers
Scadaflex II Communication Register List
Modbus Holding Registers | DF1 Bank 17 | Description
1 | 1 | AO Registers
801 | 3 | Local PI Totalizer (PI1 & PI2 ) [32 Bit]
805 | 7 | Pump Controller Starts (Pump 1,2,3) [32 Bit]
811 | 13 | Pump Controller Runtime (Pump 1,2,3) [32 Bit]
1001 | 101 | I Registers (1 - 504)
5001 | 605 | Protection Register
5002 | 606 | DO PWM On (1-4)
5006 | 610 | DO PWM Off (1-4)
5010 |  | DI Get Time
5011 |  | A/B Selector
5012 |  | DO Flash rate (x 0.01Sec)
5013 |  | AI Force Value
5017 |  | AO Force Value
5019 |  | UI NonLinear Scaling IO High - NLS 01
5020 |  | UI NonLinear Scaling IO High - NLS 02
5021 |  | UI NonLinear Scaling IO Low- NLS 01
5022 |  | UI NonLinear Scaling IO Low- NLS 02
5023 |  | UI NonLinear Scaling (21 x 2)
5065 |  | PI Filters (mS) (1 & 2)
5067 |  | DO Output Holdoff Time
5071 |  | PC Setpoints (Lead,Lag,Lag2: On/Off)
5077 |  | PC Setpoints (B) (Lead,Lag,Lag2: On/Off)
5083 |  | PC Setpoint ON Debounce
5084 |  | PC Setpoint OFF Debounce
5085 |  | PC Setpoint ON (B) Debounce
5086 |  | PC Setpoint OFF (B) Debounce
5087 |  | Master Poll Interval (100ms) - Serial
5088 |  | Master Poll Interval (S) - Cell
5089 |  | Master Poll Interval (100ms) - Ethernet
5090 |  | Master Low Power Poll Interval (100ms) Ser
5091 |  | Master Low Power Poll Interval (100ms) Cell
5092 |  | Master Low Power Poll Interval (100ms) Ethernet
5093 |  | Master Comm Fail Probe Time (S) Ser
5094 |  | Master Comm Fail Probe Time (S) Cell
5095 |  | Master Comm Fail Probe Time (S) Ethernet
5096 |  | Master Retrigger Holdoff (S) - Serial
5097 |  | Master Retrigger Holdoff (S) - Cell
5098 |  | Master Retrigger Holdoff (S) - Ethernet
5099 |  | Master Respose Timeout (0.1 Sec) - Serial
5100 |  | Master Respose Timeout (0.1 Sec) - Cell
5101 |  | Master Respose Timeout (0.1 Sec) - Ethernet
5102 |  | Master Quiet Time (ms) - Serial
5103 |  | Master Max Latency (1-32)
5135 |  | Master Destination Address (1-32)
5167 |  | Master Destination Hop 1 (1-32)
5199 |  | Master Destination Hop 2 (1-32)
5231 |  | Master Destination Hop 3 (1-32)
5263 |  | Master Destination Hop 4 (1-32)
5295 |  | Master Message Local Index (1-100)
5455 |  | Master Message Remote Index (1-100)
5615 |  | Destination Port Overide (1-32)
5647 |  | Encryption Key (16 Chars)
5655 |  | Web Refresh
5656 |  | Local AI Sensor Sleep Time
5657 |  | Local AI Sensor Warmup time
5658 |  | IO Test Speed (x 0.1 Sec)
5659 |  | Comm Buffer Limit
5660 |  | Float Fail Shutdown Timer(x I Min)
5661 |  | SMS Alarm Retry Timer
5662 |  | DNS Lookup Holdoff (S)
5663 |  | Logging - TimeBase Selector
5664 |  | Vin Low Alarm Level ( x 0.1 Volts)
5665 |  | ScaleBlock Unit Label(4 Chars) (1-66)
5797 |  | ScaleBlock Unit Label(4 Chars) (67-70)
5805 |  | ScaleBlock IO High (1-32)
5837 |  | ScaleBlock IO Low (1-32)
5869 |  | ScaleBlock Engineering High (1-32)
5901 |  | ScaleBlock Engineering Low (1-32)
5933 |  | ScaleBlock 200SS Temp Constant (1-4)
5937 |  | PID P Gain (x 1000)
5939 |  | PID I Gain (x 1000)
5941 |  | PID D Gain (x 1000)
5943 |  | PID Input Span
5945 |  | PID Output DeadBand ( x100)
5947 |  | PID Duty Cycle (S)
5949 |  | PID I/D time (x10mS)
5951 |  | SmartFlow - Pump A Flow
5952 |  | SmartFlow - Pump B Flow
5953 |  | SmartFlow - Combined Pump A&B Flow
5954 |  | SmartFlow - Level Scale
5955 |  | SmartFlow Unit Label(4 Char)
5957 |  | Trace Selector (1-63)
6020 |  | Xbee Slave Selector
6021 |  | Xbee Slave I In Offset
6022 |  | Xbee Slave B In Offset
6023 |  | AO ComFail Values
6025 |  | Friendly IP Filtering (4 Octet) (1-32)
6084 |  | Remote Sensor AI OnChange Timer (mS) (1-64)
6148 |  | DO Mode (1-4)
6152 |  | Link to DO Selector (1-4)
6156 |  | AI Mode Selector (1-4)
6160 |  | AI Speed Selector (1-4)
6164 |  | AO Mode Selector (1-2)
6166 |  | AO Link Selector (1-2)
6168 |  | PI Wiegand Mode/Map Selector
6169 |  | PC Lead / Lag Setpoint Source Index
6170 |  | PC Lead / Lag Setpoint Source B Index
6171 |  | Master Mode Retries - Serial
6172 |  | Master Mode Retries - Cell
6173 |  | Master Mode Retries -Ethernet
6174 |  | Master Message Destination Selector (1-100)
6334 |  | Master Message Type (1-100)
6494 |  | Master Message Block Size (1-100)
6654 |  | Destination Protocol Selector (1-32)
6686 |  | I Register Scaling Block Selector (1-504)
7190 |  | Trace - Strip Chart Interval
7191 |  | Trace Graph Display Style Selector
7192 |  | Trace - Color Selector Trace (1-63)
7255 |  | Trace - Style Selector Trace (1-63)
7318 |  | Trace - Group Enables (1-63)
7381 |  | Current User Page Trend Group
7382 |  | POP3 Poll time (M)
7383 |  | Alarming POP3 Poll time (M)
7384 |  | Command POP3 Poll time (M)
7385 |  | Command POP3 Poll time Period (M)
7386 |  | Sensor Power Selector
7387 |  | PumpControl Alternation / Control Scheme
7388 |  | PC1 & 2 Shutdown Select A
7389 |  | PC1 & 2 Shutdown Select B
7390 |  | A Schedule Start Time (Hours)
7391 |  | A Schedule Start Time (Minutes)
7392 |  | B Schedule Start Time (Hours)
7393 |  | B Schedule Start Time (Minutes)
7394 |  | Pump Fail Input Selector
7397 |  | Pump Auto Input Selector
7400 |  | Pump Controller Handoff
7403 |  | PID Input Selector
7405 |  | PID Setpoint Selector
7407 |  | PID Enable/Hold Selector
7409 |  | SmartFlow Tank Level Selector
7410 |  | SmartFlow Pump A Selector
7411 |  | SmartFlow Pump B Selector
7412 |  | SmartFlow Output Selector
7413 |  | Alive Message Hour Selector
7414 |  | include HMI Page in Alarm Msg Selector
7415 |  | Status Alert Message Hour
7416 |  | Status Alert Message Time Interval Selector
7417 |  | Ack All Alarms with B Register
7418 |  | Status Alert Message Enable Selector
7419 |  | Alarm Retry Counts
7420 |  | Alarm Ack ALL with DI Selector
7421 |  | Alarm Group Enables (1 per Group)
8179 |  | HMI Boolean ON Verbage (1-50)
8229 |  | HMI Boolean OFF Verbage (1-50)
8279 |  | HMI Boolean Color for Verbage (1-16)
8295 |  | LCD Contrast
8296 |  | LCD Backlight Timer
8297 |  | ScaleBlock Format Selector SB (1-66)
8363 |  | ScaleBlock 200SS Temp Selector (1-4)
8367 |  | AI Scaling Block Selector
8371 |  | Alarming E-mail Mode Selector
8372 |  | Cell Data Stats Snapshot Day of Month
8373 |  | Programming Lines per Scan
8374 |  | Web Interface Selector
8375 |  | Remote Sensor Polling ComFail Threshold
8376 |  | Remote Sensor Sleep ComFail Threshold
8377 |  | Remote Sensor PFI Polling Cycle Skip
8378 |  | Dynamic DNS Selector / Enable
8379 |  | Remote Sensor Calibration Address
8380 |  | Remote Sensor Calibration Channel
8381 |  | Remote Sensor Setup Address
8382 |  | Remote Sensor Block Size
8383 |  | Sensor Power Time (x 100mS) - Remote Sensor 1
8384 |  | Radio Tx Power - Remote Sensor 1
8385 |  | R1-R4 OC Delta - Remote Sensor 1-4
8386 |  | AI5-AI8 OC Delta - Remote Sensor 5-8
8387 |  | Mode/Config Reg 1
8388 |  | Mode/Config Reg 2
8389 |  | Mode/Config Reg 3
8390 |  | Mode/Config Reg 4
8391 |  | Mode/Config Reg 5
8392 |  | Mode/Config Reg 6
8393 |  | Mode/Config Reg 7
8394 |  | Mode/Config Reg 8
8395 |  | Remote Sensor Config Block (2-64)
9151 |  | FTP Interval Selector
9152 |  | FTP Start Time Selector
9153 |  | FTP File Mode Selector
9154 |  | FTP TrendLog Resolution Selector
9155 |  | FTP Data Selector
9156 |  | Bad Login Limit ( Number of times before lockout)
9157 |  | Bad Login Lockout Time (M)
9158 |  | Daylight Savings Dates
10000 |  | IP Address (4 Char)
10002 |  | Gate Address (4 Char)
10004 |  | Subnet Mask (4 Char)
10006 |  | DNS Address
10008 |  | Ethernet Modbus Port
10009 |  | Ethernet SDX Port
10011 |  | HTTP Port
10012 |  | SDX Unit ID
10013 |  | Ethernet Modbus / DF1 Address
10014 |  | Ethernet Comm Watchdog Timeout( x 0.1 Sec)
10015 |  | Serial Baud Rate Select
10016 |  | Serial Parity (0=None, 1 = Even, 2 = Odd)
10017 |  | Serial Rx Character Gap Extra (x 307uS)
10018 |  | Serial Xmit En Delay (0.001 S)
10019 |  | Serial Modbus / DF1 Address
10020 |  | Serial Str/Fwd In Base Add
10021 |  | Serial Str/Fwd Out Base Add
10022 |  | Serial Str/Fwd Add Range
10023 |  | Serial Comm Watchdog Timeout( x 0.1 Sec)
10024 |  | Cell Baud Rate Select
10025 |  | Cell Data Modbus Port
10026 |  | Cell Data SDX Port
10027 |  | Cell Data Web Port
10028 |  | Cell Data Mode Modbus ID
10029 |  | Cell Tower Link Fail delay (S)
10030 |  | Cell Rcvd Message TimeStamp Offset (H)
10031 |  | Cell Old Message TimeOut (M)
10032 |  | Cell Comm Watchdog Timeout( x 0.1 Sec)
10033 |  | Trace - Strip Chart Minutes
10034 |  | Remote Sensor Sleep Time (S)
10035 |  | Remote Sensor Scan HoldOff (S)
10036 |  | Remote Sensor First Address
10037 |  | Remote Sensor Response TimeOut (x100mS)
10038 |  | RemoteSensor Probe time
10039 |  | Remote Sensor Poll time
10040 |  | DI9 Interval Watchdog
10041 |  | DI10 Interval Watchdog
10042 |  | Cell Modem WEB User Refresh (S)
10043 |  | TCP Activity Timeout
10044 |  | Cellular Tower Wakup Ping (S)
10045 |  | CSV Days
10046 |  | CSV Download Default Resolution Selector
10047 |  | Alarm Group Select
10048 |  | Pump Timer
10049 |  | Pump Run timer
10050 |  | LCD Mode
10051 |  | SMS ReAlarm timer
10052 |  | Monitor Selector
10053 |  | Xbee Slave Comm Watchdog Timeout
10054 |  | Reserved for Future use
10093 |  | Last ELOG entry for Attachments
10095 |  | Remote Sensor Calibration Value
10096 |  | Restarts
10097 |  | RTC Month mm (Jan = 1)
10098 |  | RTC Day dd
10099 |  | RTC Year yy ( 2 digit year)
10100 |  | RTC Hours hh
10101 |  | RTC Minutes mm
10102 |  | RTC Seconds ss
10103 |  | TimeZone Offset ( Hours x 10)
10104 |  | Controller Name (32 Chars)
10120 |  | Control Register
10121 |  | MAC
10124 |  | Defaults Revision ID
10125 |  | Firmware Revision ID
10126 |  | Model Number
10127 |  | Bootloader Version
10128 |  | Manufacturer Date
10129 |  | Factory Cal Date
10130 |  | User Cal Date
10131 |  | SDX Buffer Size (x128 Bytes)
10132 |  | Configuration
10133 |  | Serial Number [32 Bit]
10135 |  | Manufacturer ID [32 Bit]
10137 |  | Revision Number
10142 |  | Calibration - VBATT, VIN
10144 |  | Calibration - AI Current (1-4)
10148 |  | Calibration - AO Current (1-2)
10150 |  | Calibration - AO Offset (1-2)
10152 |  | Calibration - AI Voltage
10153 |  | Calibration - AI mV
10154 |  | Calibration - AI mV Offset
10155 |  | Calibration - AI Resistive (1-4)
65001 |  | RTC Month mm (Jan = 1)
65002 |  | RTC Day dd
65003 |  | RTC Year yyyy ( 4 digit year)
65004 |  | RTC Hours hh
65005 |  | RTC Minutes mm
65006 |  | RTC Seconds ss