## ReadOnly Bits
Scadaflex II SCxR Communication Register List
Modbus Input Points | DF1 Bank 3 | Description
1 | 1 | Local DI's
13 | 13 | Pulse Inputs
15 | 15 | Charger Disable
5001 | 17 | Com Fail Status
5009 | 25 | Destination ComFail
5041 | 57 | Pump Outputs
5044 | 60 | Pump Error
5045 | 61 | Log Run Indicator
5046 | 62 | Basic First Scan
5047 | 63 | Basic Run Indicator
5048 | 64 | Alarm Active (ALL groups)
5049 | 65 | Alarm Active (per group)
5057 | 73 | DO Relay State
5061 | 77 | Local Force Enables
5065 | 81 | Alarm Bits
5633 | 649 | FTP Error
5634 | 650 | Lockout

## Bits
Scadaflex II SCxR Communication Register List
Modbus Coils | DF1 Bank 13 | Description
1 | 1 | DO (1-4)
1001 | 101 | B Registers ( 1 - 504)
5001 |  | Alarm Acknowledge Bits
5569 |  | Com Stats Clear
5570 |  | DI Totalizer Clear
5572 |  | Pump Run Starts Clear
5574 |  | Ethernet Master Comm Trigger
5575 |  | Serial Master Comm Trigger
5576 |  | Cell Master Comm Trigger
5577 |  | Radio Master Comm Trigger
5585 |  | Event Trigger (1-32)
5617 |  | Command Triggers (1-16)
5633 |  | DO Force Enable
5641 |  | DO Force Value
5649 |  | DI Force Enable
5665 |  | DI Force Value
5681 |  | AI Force Enable
5689 |  | AO Force Enable
5697 |  | DI Invert
5713 |  | Set DO on Comm Fail - DO 01
5721 |  | ComFail DO Value
5729 |  | Digital Test Mode Enable
5730 |  | Disable WAN HTTP Config Service
5731 |  | Show Forcing on Local IO Page
5732 |  | TFTP Enable
5733 |  | Ethernet Master Use Retries on Probing
5734 |  | Serial Master Use Retries on Probing
5735 |  | Cell Master Use Retries on Probing
5736 |  | Slow Trending ( Trend every 8 seconds)
5737 |  | Enable VPII Buzzer on Alarm
5738 |  | External HMI Force Enable
5739 |  | Remote HMI - Enable Buttons
5740 |  | Remote HMI - Enable Setpoint edit
5741 |  | Use DHCP
5742 |  | Allow Unsecured WUI Read Only Access
5743 |  | Low Power Enable
5744 |  | Trace - Strip Mode Enabled
5745 |  | Temp C / F
5746 |  | Use Local time in Trend files
5747 |  | Daylight Savings Time Enable
5748 |  | Allow off Schedule Acks
5749 |  | Include Acked Alarms in Messages
5750 |  | Show Idle Alarms on Website
5751 |  | Enable the All I Page
5752 |  | Enable the All B Page
5753 |  | Write Enable the All I Page
5754 |  | Write Enable the All B Page
5755 |  | Show kPa in ##.# format
5756 |  | Ethernet Auto PowerDown
5757 |  | European Mode Enable
5758 |  | PID 1 Reverse Acting
5759 |  | PID 2 Reverse Acting
5760 |  | Alive Message - Skip if Alarmed in last 24 hours
5761 |  | Display Underscore as Space
5762 |  | Ethernet: Use HTTP Accelerator
5763 |  | CellData: Use HTTP Accelerator
5764 |  | WEB Debug Enable
5765 |  | Enable Command Cell Logging
5766 |  | Enable SDX Cell Logging
5767 |  | Text Message Interface "?" - Vin Enable
5768 |  | Text Message Interface "?" - Cell RSSI Enable
5769 |  | Report on Cleared Alarms
5770 |  | Add Alarms to Cleared Report
5771 |  | Analog Test Mode Enable
5772 |  | Only except SMS/ Email Messages from Known Contacts
5773 |  | Log Diagnostics to Event Log
5774 |  | Enable Debug Mode
5775 |  | On Pump Fail Leave Call On
5776 |  | FTP Use CellData
5777 |  | Create Error/Journal Logs Oldest to Newest
5778 |  | Adjust Rcvd Message TimeStamp for DST
5779 |  | SMTP Use AUTH
5780 |  | Notification Trigger
5781 |  | FTP Trigger
5782 |  | Do Not Parse "rpt" files
5783 |  | Switch Test
5784 |  | Include Template Report
5785 |  | SMS Notify include Page 0 (Home)
5786 |  | SMS Notify include Page 1
5787 |  | SMS Notify include Page 2
5788 |  | SMS Notify include Page 3
5789 |  | SMS Notify include Page 4
5790 |  | FTP Error Log
5791 |  | FTP Event Log
5792 |  | FTP Journal
5793 |  | AO ComFail Enables
5795 |  | FTP Preface file name with unit Name
5796 |  | Allow Unsecured Log GET's
5797 |  | Mesh Polling Trigger
5798 |  | Cell DNS Overide w/ Ethernet Address
5799 |  | Radio Use Retries on Probing
5801 |  | Ethernet Port SDX Enable
5802 |  | Ethernet Port Modbus Enable
5807 |  | Ethernet VPII Enable
5809 |  | Serial Port SDX Enable
5810 |  | Serial Port Modbus Enable
5811 |  | Serial Port DF1 Enable
5817 |  | Cell Port SDX Enable
5818 |  | Cell Port Modbus Enable
5821 |  | Texting Mode Enable
5822 |  | Cell Port STM Enable
5825 |  | Radio Port SDX Enable
5826 |  | Radio Port Modbus Enable
5827 |  | Radio Port DF1 Enable
5833 |  | Display Item on ? ConcentratorDI's
5849 |  | Display Item on ? Concentrator DO's
5857 |  | Display Item on ? Concentrator AI's
5865 |  | Display Item on ? Concentrator AO's
5873 |  | Display Item on ? Concentrator B's
6377 |  | Display Item on ? Concentrator I's
6881 |  | Concentrator I Retain Enable's
7009 |  | Concentrator B Retain Enable's
7073 |  | Include HMI Item in LCD scan mode
7129 |  | Logging Attach to Right Axis Trace 1-64
7193 |  | Master Engine Destination Disable
7225 |  | ScaleBlock Unsignd/Signed Selector 1-32
7257 |  | Disable 'Full Website' on Mobile
7258 |  | Disable 'Trend' on Mobile
7259 |  | Disable 'Alarms' on Mobile
7260 |  | Enable 'Graphic HMI' on Mobile
7265 |  | Concentrator Bit Write Enable B's
7769 |  | Concentrator Integer Write Enable I's
8273 |  | Display Item on WEB Concentrator B's
8777 |  | Display Item on WEB Concentrator I's
9281 |  | Display Item on WEB User Commands
9297 |  | Site CheckIn Alarm Group Enable (1-8)
9305 |  | Status Alert Alarm Group Enable (1-8)

## Read Only Integers
Scadaflex II SCxR Communication Register List
Modbus Input Registers | DF1 Bank 7 | Description
1 | 1 | AI Registers
5 | 5 | Internal Temperature
6 | 6 | VIN ( x100mV)
7 | 7 | VBATT ( x100mV)
5001 | 8 | PI Rate (1 & 2)
5003 | 10 | PI Interval (1 & 2) [ 2 x 32 Bit]
5007 | 14 | Ethernet Slave TX/RX Packets [ 2 x 32 Bit]
5011 | 18 | Serial Slave TX/RX Packets [ 2 x 32 Bit]
5015 | 22 | Radio Slave TX/RX Packets [ 2 x 32 Bit]
5019 | 26 | Cell Slave TX/RX Packets [ 2 x 32 Bit]
5023 | 30 | Master Destination TX/RX Packets [ 2 x 32 Bit] (1-32)
5151 | 158 | Current Cell Data TX/RX Bytes [ 2 x 32 Bit]
5155 | 162 | Last Month Cell Data TX/RX Bytes [ 2 x 32 Bit]
5159 | 166 | Current Month Cell SMS TX/RX Bytes [ 2 x 32 Bit]
5163 | 170 | Last Month Cell SMS TX/RX Bytes [ 2 x 32 Bit]
5167 | 174 | Master Success - Ethernet %
5168 | 175 | Master Success - Serial %
5169 | 176 | Master Success - Radio %
5170 | 177 | Master Success - Cell %
5171 | 178 | Cell phone Signal Strength (RSSI)
5172 | 179 | VIN ( x100mV)
5173 | 180 | Last SDX Error Code
5174 | 181 | Last Error Extension
5175 | 182 | Last Source Address - Ethernet
5176 | 183 | Last Source Address - Serial
5177 | 184 | Last Source Address - Radio
5178 | 185 | Last Source Address - Cell
5179 | 186 | Last Destination Address - Ethernet
5180 | 187 | Last Destination Address - Serial
5181 | 188 | Last Destination Address - Radio
5182 | 189 | Last Destination Address - Cell
5183 | 190 | Last Source Address for us - Ethernet
5184 | 191 | Last Source Address for us - Serial
5185 | 192 | Last Source Address for us - Radio
5186 | 193 | Last Source Address for us - Cell
5187 | 194 | Destination Com Fail Counts (1-32)
5219 | 226 | Ethernet Com Fail Counts
5220 | 227 | Serial Com Fail Counts
5221 | 228 | Cell Com Fail Counts
5222 | 229 | Radio Com Fail Counts
5223 | 230 | Ethenet Slave Latency Live
5224 | 231 | Ethenet Slave Latency Last
5225 | 232 | Ethenet Slave Latency Max
5226 | 233 | Serial Slave Latency Live
5227 | 234 | Serial Slave Latency Last
5228 | 235 | Serial Slave Latency Max
5229 | 236 | Cell Slave Latency Live
5230 | 237 | Cell Slave Latency Last
5231 | 238 | Cell Slave Latency Max
5232 | 239 | Radio Slave Latency Live
5233 | 240 | Radio Slave Latency Last
5234 | 241 | Radio Slave Latency Max
5235 | 242 | Destination Latency Last (1-32)
5267 | 274 | Systick [32 bit]
5269 | 276 | Programming Scan Time
5270 | 277 | Programming Scan Time MAX
5271 | 278 | Programming Error Code
5272 | 279 | Programming Error Line
5274 | 281 | Journal Stats (% used)
5275 | 282 | Event Log Stats (% used)
5276 | 283 | Error Log Stats (% used)
5277 | 284 | PID Error (1 & 2 )
5279 | 286 | PID Output (1 & 2 )
5281 | 288 | PID DeadBand Output (1 & 2 )
5283 | 290 | PID P Out [32 Bit] (1 & 2 )
5287 | 294 | PID I Out [32 Bit] (1 & 2 )
5291 | 298 | PID D Out [32 Bit] (1 & 2 )
5295 | 302 | CellData Debug Stats

## Integers
Scadaflex II SCxR Communication Register List
Modbus Holding Registers | DF1 Bank 17 | Description
1 | 1 | AO Registers
801 | 3 | Local PI Totalizer (PI1 & PI2 ) [32 Bit]
805 | 7 | Pump Controller Starts (Pump 1,2,3) [32 Bit]
811 | 13 | Pump Controller Runtime (Pump 1,2,3) [32 Bit]
1001 | 101 | I Registers (1 - 504)
5001 | 605 | Protection Register
5002 | 606 | DO PWM On (1-4)
5006 | 610 | DO PWM Off (1-4)
5010 |  | DI Get Time
5011 |  | A/B Selector
5012 |  | DO Flash rate (x 0.01Sec)
5013 |  | AI Force Value
5017 |  | AO Force Value
5019 |  | UI NonLinear Scaling IO High - NLS 01
5020 |  | UI NonLinear Scaling IO High - NLS 02
5021 |  | UI NonLinear Scaling IO Low- NLS 01
5022 |  | UI NonLinear Scaling IO Low- NLS 02
5023 |  | UI NonLinear Scaling (21 x 2)
5065 |  | PI Filters (mS) (1 & 2)
5067 |  | DO Output Holdoff Time
5071 |  | PC Setpoints (Lead,Lag,Lag2: On/Off)
5077 |  | PC Setpoints (B) (Lead,Lag,Lag2: On/Off)
5083 |  | PC Setpoint ON Debounce
5084 |  | PC Setpoint OFF Debounce
5085 |  | PC Setpoint ON (B) Debounce
5086 |  | PC Setpoint OFF (B) Debounce
5087 |  | Master Poll Interval (100ms) - Serial
5088 |  | Master Poll Interval (100ms) - Radio
5089 |  | Master Poll Interval (S) - Cell
5090 |  | Master Poll Interval (100ms) - Ethernet
5091 |  | Master Low Power Poll Interval (100ms) Ser
5092 |  | Master Low Power Poll Interval (100ms) Radio
5093 |  | Master Low Power Poll Interval (100ms) Cell
5094 |  | Master Low Power Poll Interval (100ms) Ethernet
5095 |  | Master Comm Fail Probe Time (S) Ser
5096 |  | Master Comm Fail Probe Time (S) Radio
5097 |  | Master Comm Fail Probe Time (S) Cell
5098 |  | Master Comm Fail Probe Time (S) Ethernet
5099 |  | Master Retrigger Holdoff (S) - Serial
5100 |  | Master Retrigger Holdoff (S) - Radio
5101 |  | Master Retrigger Holdoff (S) - Cell
5102 |  | Master Retrigger Holdoff (S) - Ethernet
5103 |  | Master Respose Timeout (0.1 Sec) - Serial
5104 |  | Master Respose Timeout (0.1 Sec) - Radio
5105 |  | Master Respose Timeout (0.1 Sec) - Cell
5106 |  | Master Respose Timeout (0.1 Sec) - Ethernet
5107 |  | Master Quiet Time (ms) - Serial
5108 |  | Master Quiet Time (ms) - Radio
5109 |  | Master Max Latency (1-32)
5141 |  | Master Destination Address (1-32)
5173 |  | Master Destination Hop 1 (1-32)
5205 |  | Master Destination Hop 2 (1-32)
5237 |  | Master Destination Hop 3 (1-32)
5269 |  | Master Destination Hop 4 (1-32)
5301 |  | Master Message Local Index (1-100)
5461 |  | Master Message Remote Index (1-100)
5621 |  | Destination Port Overide (1-32)
5653 |  | Encryption Key (16 Chars)
5661 |  | Web Refresh
5662 |  | Local AI Sensor Sleep Time
5663 |  | Local AI Sensor Warmup time
5664 |  | IO Test Speed (x 0.1 Sec)
5665 |  | Comm Buffer Limit
5666 |  | Float Fail Shutdown Timer(x I Min)
5667 |  | SMS Alarm Retry Timer
5668 |  | DNS Lookup Holdoff (S)
5669 |  | Logging - TimeBase Selector
5670 |  | Vin Low Alarm Level ( x 0.1 Volts)
5671 |  | ScaleBlock Unit Label(4 Chars) (1-66)
5803 |  | ScaleBlock Unit Label(4 Chars) (67-70)
5811 |  | ScaleBlock IO High (1-32)
5843 |  | ScaleBlock IO Low (1-32)
5875 |  | ScaleBlock Engineering High (1-32)
5907 |  | ScaleBlock Engineering Low (1-32)
5939 |  | ScaleBlock 200SS Temp Constant (1-4)
5943 |  | PID P Gain (x 1000)
5945 |  | PID I Gain (x 1000)
5947 |  | PID D Gain (x 1000)
5949 |  | PID Input Span
5951 |  | PID Output DeadBand ( x100)
5953 |  | PID Duty Cycle (S)
5955 |  | PID I/D time (x10mS)
5957 |  | SmartFlow - Pump A Flow
5958 |  | SmartFlow - Pump B Flow
5959 |  | SmartFlow - Combined Pump A&B Flow
5960 |  | SmartFlow - Level Scale
5961 |  | SmartFlow Unit Label(4 Char)
5963 |  | Trace Selector (1-63)
6026 |  | AO ComFail Values
6028 |  | DO Mode (1-4)
6032 |  | Link to DO Selector (1-4)
6036 |  | AI Mode Selector (1-4)
6040 |  | AI Speed Selector (1-4)
6044 |  | AO Mode Selector (1-2)
6046 |  | AO Link Selector (1-2)
6048 |  | PI Wiegand Mode/Map Selector
6049 |  | PC Lead / Lag Setpoint Source Index
6050 |  | PC Lead / Lag Setpoint Source B Index
6051 |  | Master Mode Retries - Serial
6052 |  | Master Mode Retries - Radio
6053 |  | Master Mode Retries - Cell
6054 |  | Master Mode Retries -Ethernet
6055 |  | Master Message Destination Selector (1-100)
6215 |  | Master Message Type (1-100)
6375 |  | Master Message Block Size (1-100)
6535 |  | Destination Protocol Selector (1-32)
6567 |  | I Register Scaling Block Selector (1-504)
7071 |  | Trace - Strip Chart Interval
7072 |  | Trace Graph Display Style Selector
7073 |  | Trace - Color Selector Trace (1-63)
7136 |  | Trace - Style Selector Trace (1-63)
7199 |  | Trace - Group Enables (1-63)
7262 |  | Current User Page Trend Group
7263 |  | POP3 Poll time (M)
7264 |  | Alarming POP3 Poll time (M)
7265 |  | Command POP3 Poll time (M)
7266 |  | Command POP3 Poll time Period (M)
7267 |  | Sensor Power Selector
7268 |  | PumpControl Alternation / Control Scheme
7269 |  | PC1 & 2 Shutdown Select A
7270 |  | PC1 & 2 Shutdown Select B
7271 |  | A Schedule Start Time (Hours)
7272 |  | A Schedule Start Time (Minutes)
7273 |  | B Schedule Start Time (Hours)
7274 |  | B Schedule Start Time (Minutes)
7275 |  | Pump Fail Input Selector
7278 |  | Pump Auto Input Selector
7281 |  | Pump Controller Handoff
7284 |  | PID Input Selector
7286 |  | PID Setpoint Selector
7288 |  | PID Enable/Hold Selector
7290 |  | SmartFlow Tank Level Selector
7291 |  | SmartFlow Pump A Selector
7292 |  | SmartFlow Pump B Selector
7293 |  | SmartFlow Output Selector
7294 |  | Alive Message Hour Selector
7295 |  | include HMI Page in Alarm Msg Selector
7296 |  | Status Alert Message Hour
7297 |  | Status Alert Message Time Interval Selector
7298 |  | Ack All Alarms with B Register
7299 |  | Status Alert Message Enable Selector
7300 |  | Alarm Retry Counts
7301 |  | Alarm Ack ALL with DI Selector
7302 |  | Alarm Group Enables (1 per Group)
8060 |  | HMI Boolean ON Verbage (1-50)
8110 |  | HMI Boolean OFF Verbage (1-50)
8160 |  | HMI Boolean Color for Verbage (1-16)
8176 |  | LCD Contrast
8177 |  | LCD Backlight Timer
8178 |  | ScaleBlock Format Selector SB (1-66)
8244 |  | ScaleBlock 200SS Temp Selector (1-4)
8248 |  | AI Scaling Block Selector
8252 |  | Alarming E-mail Mode Selector
8253 |  | Cell Data Stats Snapshot Day of Month
8254 |  | Programming Lines per Scan
8255 |  | Web Interface Selector
8256 |  | Dynamic DNS Selector / Enable
8257 |  | FTP Interval Selector
8258 |  | FTP Start Time Selector
8259 |  | FTP File Mode Selector
8260 |  | FTP TrendLog Resolution Selector
8261 |  | FTP Data Selector
8262 |  | reserved
8263 |  | Bad Login Limit ( Number of times before lockout)
8264 |  | Bad Login Lockout Time (M)
8265 |  | Daylight Savings Dates
8269 |  | Cell Ping Enable
8270 |  | Pre-Ping Activity Timeout (S)
10000 |  | IP Address (4 Char)
10002 |  | Gate Address (4 Char)
10004 |  | Subnet Mask (4 Char)
10006 |  | DNS Address
10008 |  | Ethernet Modbus Port
10009 |  | Ethernet SDX Port
10011 |  | HTTP Port
10012 |  | SDX Unit ID
10013 |  | Ethernet Modbus / DF1 Address
10014 |  | Ethernet Comm Watchdog Timeout( x 0.1 Sec)
10015 |  | Serial Baud Rate Select
10016 |  | Serial Parity (0=None, 1 = Even, 2 = Odd)
10017 |  | Serial Rx Character Gap Extra (x 307uS)
10018 |  | Serial Xmit En Delay (0.001 S)
10019 |  | Serial Modbus / DF1 Address
10020 |  | Serial Str/Fwd In Base Add
10021 |  | Serial Str/Fwd Out Base Add
10022 |  | Serial Str/Fwd Add Range
10023 |  | Serial Comm Watchdog Timeout( x 0.1 Sec)
10024 |  | Cell Baud Rate Select
10025 |  | Cell Data Modbus Port
10026 |  | Cell Data SDX Port
10027 |  | Cell Data Web Port
10028 |  | Cell Data Mode Modbus ID
10029 |  | Cell Tower Link Fail delay (S)
10030 |  | Cell Rcvd Message TimeStamp Offset (H)
10031 |  | Cell Old Message TimeOut (M)
10032 |  | Cell Comm Watchdog Timeout( x 0.1 Sec)
10033 |  | Trace - Strip Chart Minutes
10040 |  | DI9 Interval Watchdog
10041 |  | DI10 Interval Watchdog
10042 |  | Cell Modem WEB User Refresh (S)
10043 |  | TCP Activity Timeout
10044 |  | Cellular Wakup Ping Delay (S)
10045 |  | CSV Days
10046 |  | CSV Download Default Resolution Selector
10047 |  | Alarm Group Select
10048 |  | Pump Timer
10049 |  | Pump Run timer
10050 |  | LCD Mode
10051 |  | SMS ReAlarm timer
10052 |  | Monitor Selector
10054 |  | Radio Baud Rate Select
10055 |  | Radio Parity (0=None, 1 = Even, 2 = Odd)
10056 |  | Radio Rx Character Gap Extra (x 307uS)
10057 |  | Radio Xmit En Delay (0.001 S)
10058 |  | Radio Modbus / DF1 Address
10059 |  | Radio Str/Fwd In Base Add
10060 |  | Radio Str/Fwd Out Base Add
10061 |  | Radio Str/Fwd Add Range
10062 |  | Radio Comm Watchdog Timeout( x 0.1 Sec)
10093 |  | Last ELOG entry for Attachments
10095 |  | Remote Sensor Calibration Value
10096 |  | Restarts
10097 |  | RTC Month mm (Jan = 1)
10098 |  | RTC Day dd
10099 |  | RTC Year yy ( 2 digit year)
10100 |  | RTC Hours hh
10101 |  | RTC Minutes mm
10102 |  | RTC Seconds ss
10103 |  | TimeZone Offset ( Hours x 10)
10104 |  | Controller Name (32 Chars)
10120 |  | Control Register **
10121 |  | MAC
10124 |  | Defaults Revision ID
10125 |  | Firmware Revision ID
10126 |  | Model Number
10127 |  | Bootloader Version
10128 |  | Manufacturer Date
10129 |  | Factory Cal Date
10130 |  | User Cal Date
10131 |  | SDX Buffer Size (x128 Bytes)
10132 |  | Configuration
10133 |  | Serial Number [32 Bit]
10135 |  | Manufacturer ID [32 Bit]
10137 |  | Revision Number
10138 |  | Reserved for future use
10142 |  | Calibration - VBATT, VIN
10144 |  | Calibration - AI Current (1-4)
10148 |  | Calibration - AO Current (1-2)
10150 |  | Calibration - AO Offset (1-2)
10152 |  | Calibration - AI Voltage
10153 |  | Calibration - AI mV
10154 |  | Calibration - AI mV Offset
10155 |  | Calibration - AI Resistive (1-4)
65001 |  | RTC Month mm (Jan = 1)
65002 |  | RTC Day dd
65003 |  | RTC Year yyyy ( 4 digit year)
65004 |  | RTC Hours hh
65005 |  | RTC Minutes mm
65006 |  | RTC Seconds ss