## Status ( 1xxxx )
Modulus IO Communication Register List
Modbus Status | DF1/EIP Bank 3 | Description
1 | 1 | Local DI's
33 | 33 | AI Low Alarm Bits
57 | 57 | AI High Alarm Bits
81 | 81 | Com Fail Status
89 | 89 | Destination ComFail (1-32)
121 | 121 | IO Buss Master Destination ComFail (1-32)
153 | 153 | IO Buss Master Redundant ComFail (1-32)
185 | 185 | IO Buss Master Redundant Active (1-32)
217 | 217 | Pump Error (1-3)
220 | 220 | Pump Controller Error
221 | 221 | Programming Severe Error
222 | 222 | Hardware Fault
223 | 223 | Software Fault
224 | 224 | Network Fault
233 | 233 | Local Force Status
237 | 237 | Basic First Scan
238 | 238 | Basic Run Indicator
239 | 239 | FTP Server file received
240 | 240 | Lockout
241 | 241 | Com Master Config Error Flags
249 | 249 | DO Relay State (1-24)
273 | 273 | Alarm Active (per group)
281 | 281 | Alarming
282 | 282 | Log Run Indicator
305 | 305 | Fault Bits

## Coils ( 0xxxx )
Modulus IO Communication Register List
Modbus Coils | DF1/EIP Bank 13 | Description
1 | 1 | Local DO's
33 | 33 | PI Totalizer Clear
41 | 41 | Backplane Serial Com Stats Clear
42 | 42 | Ethernet Com Stats Clear
43 | 43 | Com1 Com Stats Clear
44 | 44 | Com2 Com Stats Clear
48 | 48 | Delete Cleared Alarms
49 | 49 | Command Triggers (1-16)
65 | 65 | TestAlarm Trigger
101 | 101 | B Registers ( 1 - 504)
605 |  | FTP Logging Trigger
606 |  | Backplane Serial Master Comm Trigger
607 |  | Ethernet Master Comm Trigger
608 |  | Com1 Master Comm Trigger
609 |  | Com2 Master Comm Trigger
610 |  | MQTT Publish All Trigger
611 |  | Report Trigger
612 |  | Error Stack Clear
613 |  | Comm Event Trigger (1-128)
741 |  | IO Buss Event Trigger (1-128)
2001 |  | Daylight Savings Time Enable
2009 |  | IO Force Enable
2033 |  | IO Comm Fail Enables ( DO & AO )
2057 |  | DI Invert
2081 |  | DI Filter Enable (DI9 - DI24)
2097 |  | Digital Test Mode Enable
2098 |  | Analog Test Mode Enable
2099 |  | Disable WAN HTTP Config Service
2100 |  | Time Master
2101 |  | TFTP Enable
2103 |  | Allow Unsecured Log GET's
2104 |  | Use DHCP
2105 |  | Allow Unsecured WUI Read Only Access
2106 |  | Disable Config Register Write Protection
2107 |  | Ethernet Auto PowerDown
2108 |  | Use STARTTLS on Port 587 ( Microsoft Servers )
2109 |  | Temp C / F
2110 |  | Enable IOX Alarming Client System
2111 |  | Ethernet: Use HTTP Accelerator
2112 |  | Enable Debug Mode
2113 |  | Display Underscore as Space
2114 |  | Disable Modbus Redirect on IO Buss
2115 |  | Disable Web Redirect on IO Buss
2119 |  | Ping Disable
2120 |  | Enable IOX Alarming Server System
2121 |  | Attempt Programming Restart on Error
2122 |  | Programming ScanTime WatchDog Disable
2125 |  | Disable 'Full Website' on Mobile
2126 |  | Enable 'Graphic HMI' on Mobile
2127 |  | Enable High Speed Analog's
2128 |  | Link Layer Disable
2129 |  | PID Reverse Acting Channel 1
2130 |  | PID Reverse Acting Channel 2
2131 |  | PID Reverse Acting Channel 3
2132 |  | PID Reverse Acting Channel 4
2133 |  | Enable Both Float & Level Controller on Local Display
2134 |  | Alive Message - Skip if Alarmed in last 24 hours
2135 |  | On Pump Fail Leave Call On
2137 |  | BackPlane Master Use Retries on Probing
2138 |  | Ethernet Master Use Retries on Probing
2139 |  | Com1 Master Use Retries on Probing
2140 |  | Com2 Master Use Retries on Probing
2142 |  | Programming AutoStart
2144 |  | MQTT Use Secure TLS Connection
2145 |  | Log Category Enable 0
2146 |  | Log Category Enable 1
2147 |  | Log Category Enable 2
2148 |  | Log Category Enable 3
2149 |  | Log Category Enable 4
2150 |  | Log Category Enable 5
2151 |  | Log Category Enable 6
2152 |  | Log Category Enable 7
2153 |  | Log Category Enable 8
2154 |  | Log Category Enable 9
2155 |  | Log Category Enable 10
2156 |  | Log Category Enable 11
2157 |  | Log Category Enable 12
2158 |  | Log Category Enable 13
2159 |  | Log Category Enable 14
2160 |  | Log Category Enable 15
2161 |  | FTP Preface file name with unit Name
2162 |  | Allow off Schedule Acks
2163 |  | MQTT Add Units to Published numbers
2164 |  | Add Alarms to Cleared Report
2165 |  | Only except SMS/ Email Messages from Known Contacts
2169 |  | Ethernet FTP Server Enable
2170 |  | Ethernet FTP Server Anonymous Logon allowed
2171 |  | FTP Relay from Server to Client
2172 |  | External CellModem Enable
2176 |  | Report on Cleared Alarms
2177 |  | Disable SDX Redirect on IO Buss
2178 |  | Trending Strip mode enable
2182 |  | Enable Satellite Time Update
2185 |  | Ethernet Port SDX Enable
2186 |  | Ethernet Port Modbus Enable
2187 |  | Ethernet IP Port Enable
2193 |  | Bus Port SDX Enable
2194 |  | Bus Port Modbus Enable
2195 |  | Bus Port DF1 Enable
2197 |  | Bus Bridging Eterlogic Enable
2201 |  | Com1 Port SDX Enable
2202 |  | Com1 Port Modbus Enable
2203 |  | Com1 Port DF1 enable
2204 |  | Com1 Port Bricknet enable
2205 |  | Com1 Bridging Eterlogic Enable
2209 |  | Com2 Port SDX Enable
2210 |  | Com2 Port Modbus Enable
2211 |  | Com2 Port DF1 enable
2213 |  | Com2 Bridging Eterlogic Enable
2217 |  | N Resgister Retain Enable's
2721 |  | B Register Retain Enable's
3225 |  | Master Engine Destination Disable
3257 |  | Master Engine Event Polling Enable
3385 |  | IO Buss Master Event Polling Enable
3513 |  | IO Buss Master Engine Destination Disable
3545 |  | UI Scale Clamp Enable
3569 |  | B Register Write Enables
4073 |  | N Register Write Enables
4577 |  | Display Item on WEB B Registers
5081 |  | Display Item on WEB N Registers
5585 |  | Display Item on WEB Command Triggers
5601 |  | Display Item on WEB IO
5649 |  | Display HMI Scan Enable
5681 |  | Display HMI Write Enable
5713 |  | Text HMI Page Enables
5721 |  | Trending Attach Trace to Right Axis 1-64
5785 |  | Alarm Disable Bits - B's
6289 |  | Alarm Disable Bits - DI's
6313 |  | Alarm Disable Bits - Others

## Input Registers ( 3xxxx )
Modulus IO Communication Register List
Modbus Input Registers | DF1/EIP Bank 7 | Description
1 | 1 | AI Registers
25 | 25 | Vin
27 | 27 | Internal Temperature
31 | 31 | External Cell RSSI
32 | 32 | Ultrasonic Reading
33 | 33 | AI Raw Values
65 | 65 | DI Rate 1-8
73 | 73 | DI Interval [ 32 Bit] 1-8
89 | 89 | PID Output
93 | 93 | PID Error
99 | 99 | Ethernet Slave TX/RX Packets [ 2 x 16 Bit]
101 | 101 | Backplane Slave TX/RX Packets [ 2 x 16 Bit]
103 | 103 | Com1 Slave TX/RX Packets [ 2 x 16 Bit]
105 | 105 | Com2 Slave TX/RX Packets [ 2 x 16 Bit]
107 | 107 | Master Destination TX/RX Packets [ 2 x 16 Bit] (1-32)
171 | 171 | IO Buss Master Destination TX/RX Packets [ 2 x 16 Bit] (1-32)
235 | 235 | Master Success - Backplane %
236 | 236 | Master Success - Ethernet %
237 | 237 | Master Success - Com1 %
238 | 238 | Master Success - Com2 %
239 | 239 | Last Source Address - Ethernet
240 | 240 | Last Source Address - Backplane
241 | 241 | Last Source Address - Com1
242 | 242 | Last Source Address - Com2
243 | 243 | Last Destination Address - Ethernet
244 | 244 | Last Destination Address - Backplane
245 | 245 | Last Destination Address - Com1
246 | 246 | Last Destination Address - Com2
247 | 247 | Ethernet Com Fail Counts
248 | 248 | Buss Com Fail Counts
249 | 249 | Com1 Com Fail Counts
250 | 250 | Com2 Com Fail Counts
251 | 251 | Latency Last - Ethernet
252 | 252 | Latency Last - Backplane
253 | 253 | Latency Last - Com1
254 | 254 | Latency Last - Com2
255 | 255 | Latency Max - Ethernet
256 | 256 | Latency Max - Backplane
257 | 257 | Latency Max - Com1
258 | 258 | Latency Max - Com2
259 | 259 | Destination Com Fail Counts (1-32)
291 | 291 | Destination Latency Last (1-32)
323 | 323 | IO Buss Master Destination Com Fail Counts (1-32)
355 | 355 | Latency Live - Ethernet
356 | 356 | Latency Live - Backplane
357 | 357 | Latency Live - Com1
358 | 358 | Latency Live - Com2
363 | 363 | Last System Code
368 | 368 | Last System Extension
373 | 373 | Error Stack Pointer
374 | 374 | Backplane Com UART Errors
375 | 375 | IOX Resets Received
376 | 376 | IOX Hello's Acknowledged
377 | 377 | IOX Accepts per Second
378 | 378 | IOX Tokens Received
379 | 379 | IOX Collisions
380 | 380 | IOX Next Neighbor
381 | 381 | IOX Longest Accept wait (ms)
382 | 382 | IOX Heath
383 | 383 | IOX Checksum Errors
384 | 384 | IOX Slot Status Bits
416 | 416 | LastCallerId
417 | 417 | Pump Controller Sequence ID
444 | 444 | External CellModem SMS Tx Counts
445 | 445 | External CellModem SMS Rx Counts
446 | 446 | Systick [32 bit]
448 | 448 | Programming Scan Time
449 | 449 | Programming Scan Time MAX
450 | 450 | Programming Error Code
451 | 451 | Programming Error Line
452 | 452 | Programming Error Code (clears after reading in programming)
453 | 453 | System Log Stats (% used)
454 | 454 | Event Log Stats (% used)
455 | 455 | Alarm Journal Log Stats (% used)
456 | 456 | PID P Out [32 bit]
464 | 464 | PID I Out [32 bit]
472 | 472 | PID D Out [32 bit]

## Holding Registers ( 4xxxx )
Modulus IO Communication Register List
Modbus Holding Registers | DF1/EIP Bank 17 | Description
1 | 1 | AO Registers
25 | 25 | DI Totalizers (1-8) [32 Bit]
41 | 41 | Pump Controller Starts (32Bit)
47 | 47 | Pump Controller RunTime (32Bit)
101 | 101 | N Registers (1 - 504)
605 | 605 | Protection Register
606 | 606 | UI Low Setpoint
630 | 630 | UI High Setpoint
654 | 654 | PID P Gain (x 1000)
658 | 658 | PID I Gain (x 1000)
662 | 662 | PID D Gain (x 1000)
666 | 666 | Pump Controller Lead A On Setpoint
667 | 667 | Pump Controller Lead A Off Setpoint
668 | 668 | Pump Controller Lag A On Setpoint
669 | 669 | Pump Controller Lag A Off Setpoint
670 | 670 | Pump Controller Lag2 A On Setpoint
671 | 671 | Pump Controller Lag2 A Off Setpoint
672 | 672 | Pump Controller Lead B On Setpoint
673 | 673 | Pump Controller Lead B Off Setpoint
674 | 674 | Pump Controller Lag B On Setpoint
675 | 675 | Pump Controller Lag B Off Setpoint
676 | 676 | Pump Controller Lag2 B On Setpoint
677 | 677 | Pump Controller Lag2 B Off Setpoint
678 |  | DI Gate Time
680 |  | DI Interval Watchdog
681 |  | IO Force Value
705 |  | IO Comm Fail Values
729 |  | DO Output Holdoff Time
753 |  | UI IO High (1-32)
777 |  | UI IO Low (1-32)
801 |  | UI Engineering High (1-32)
825 |  | UI Engineering Low (1-32)
849 |  | Master Poll Interval (100ms) - Backplane
850 |  | Master Poll Interval (100ms) - Ethernet
851 |  | Master Poll Interval (100ms) - Com1
852 |  | Master Poll Interval (100ms) - Com2
853 |  | Master Comm Fail Probe Time (S) Backplane
854 |  | Master Comm Fail Probe Time (S) Ethernet
855 |  | Master Comm Fail Probe Time (S) Com1
856 |  | Master Comm Fail Probe Time (S) Com2
861 |  | Master Respose Timeout (0.1 Sec) - Backplane
862 |  | Master Respose Timeout (0.1 Sec) - Ethernet
863 |  | Master Respose Timeout (0.1 Sec) - Com1
864 |  | Master Respose Timeout (0.1 Sec) - Com2
865 |  | Master Quiet Time (ms) - Backplane
866 |  | Master Quiet Time (ms) - Com1
867 |  | Master Quiet Time (ms) - Com2
868 |  | Master Max Latency (1-32)
900 |  | Master Destination Address (1-32)
932 |  | Master Destination Hop 1 (1-32)
964 |  | Master Destination Hop 2 (1-32)
996 |  | Master Message Local Index (1-128)
1124 |  | Master Message Remote Index (1-128)
1252 |  | Destination Port Overide (1-32)
1284 |  | Trend Strip Chart Display Minutes
1285 |  | Web Refresh
1286 |  | Local UI Sensor Sleep Time
1287 |  | Local UI Sensor Warmup time
1288 |  | IO Test Speed (x 0.1 Sec)
1289 |  | Comm Buffer Limit
1290 |  | DNS Lookup Holdoff (S)
1291 |  | IO Buss Polling rate
1294 |  | IOX Event Polling Time (10 mS)
1295 |  | IOX Comm Fail Probe Timer
1296 |  | MIB-NET Slice Time (mS)
1297 |  | MIB-NET Discovery Time (100 mS)
1298 |  | MIB-NET Slice TimeOut (mS)
1299 |  | IOX Event Local Index
1427 |  | IOX Event Remote Index
1555 |  | PID Input Span
1559 |  | PID I/D time (x10mS)
1563 |  | PID Output DeadBand ( x100)
1567 |  | PID Duty Cycle (S)
1571 |  | Display HMI Objects
1603 |  | Pump Controller Debouncing
1607 |  | Sensor Power Selector Object
1608 |  | Alarm Output Selector
1609 |  | Ack All Alarms with B Register
1610 |  | PID Input Selector
1614 |  | PID Enable/Hold Selector
1618 |  | PID Setpoint Selector
1622 |  | PID Analog Out Selector
1626 |  | PID Digital PWM Out Selector
1630 |  | Pump Controller Call Output Selectors
1633 |  | Pump Controller Level Source Selectors
1635 |  | Pump Controller A/B Selector
1636 |  | Pump Controller ShutOff A Selector
1637 |  | Pump Controller ShutOff B Selector
1638 |  | Pump Controller Auto Input Selectors
1641 |  | Pump Controller Run Input Selectors
1644 |  | Pump Controller Float Input Selectors
1648 |  | Pump Controller Float Failsafe Timer
1649 |  | Pump Controller Fail Shutdown Timer
1650 |  | Pump Controller Pump Failure Timer
1651 |  | Trace Selector (1-63)
1714 |  | SMS ReAlarm timer
1715 |  | Secondary Local HMI Switch Selector
1716 |  | Local HMI Switch Enable
1717 |  | C Drive Purge before days back
1718 |  | Routeing Destination Ports
1726 |  | Routeing IP Addresses
1742 |  | Routeing Listen Ports
1750 |  | PumpController Pump Fail Selectors
1753 |  | IO Mode Selector
1777 |  | UI Format Selector
1801 |  | N Register Scaling Block Selector (1-504)
2305 |  | Display Timeout (M)
2306 |  | Programming Lines per Scan
2307 |  | Web Interface Selector
2308 |  | Dynamic DNS Selector / Enable
2309 |  | Text HMI Boolean ON Verbage (1-50)
2359 |  | HMI Boolean OFF Verbage (1-50)
2409 |  | HMI Boolean Color for Verbage (1-16)
2426 |  | Master Mode Retries - Backplane
2427 |  | Master Mode Retries -Ethernet
2428 |  | Master Mode Retries -Com1
2429 |  | Master Mode Retries -Com2
2430 |  | Master Message Destination Selector
2558 |  | Master Message Type
2686 |  | Master Message Block Size
2814 |  | Destination Protocol Selector (1-32)
2846 |  | MIB-NET Max Discovery Slot
2847 |  | IOX Comfail Threshold
2848 |  | Bad Login Limit ( Number of times before lockout)
2849 |  | Bad Login Lockout Time (M)
2850 |  | Daylight Savings Dates
2854 |  | AI Alarming Hysterisis (0 - 25.5%)
2878 |  | UI Averaging Selector
2902 |  | Display HMI Boolean ON Verbage (1-32)
2934 |  | Display HMI Boolean OFF Verbage (1-32)
2966 |  | IOX Event Destination Selector
3094 |  | IOX Event BlockSize
3222 |  | IOX Event Message Type
3350 |  | PI Filters (mS)
3358 |  | IOX Redundant Slave Selector
3390 |  | Pump Controller Mode/Enable Selector
3391 |  | Pump Controller Handoff Selectors
3394 |  | Trace - Strip Chart Interval
3395 |  | Trace Graph Display Style Selector
3396 |  | Trace - Color Selector Trace (1-63)
3459 |  | Trace - Style Selector Trace (1-63)
3522 |  | Trace - Group Enables (1-63)
3585 |  | Basic Startup Delay
3586 |  | IOX Relayed Message Timeout (0.1S)
3587 |  | Alarm Ack ALL with DI Selector
3588 |  | Alarm Group Enables- B's
4092 |  | Alarm Group Enables- DI's
4116 |  | Alarm Group Enables- Local Com Fail's
4124 |  | Alarm Group Enables- Destination ComFail's
4156 |  | Alarm Group Enables- IOX Com Fail's
4157 |  | Alarm Group Enables- AI Alarms
4158 |  | Alarm Group Enables - PumpController
4159 |  | Alarm Group Enables - Programming
4160 |  | Alarm Group Enables - Faults
4163 |  | FTP Interval Selector
4164 |  | FTP Start Time Selector
4165 |  | FTP File Mode Selector
4166 |  | FTP TrendLog Resolution Selector
4167 |  | FTP Data Selector
4168 |  | Ethernet Pre-Ping (S) ##.#
4169 |  | Bridging Mode Selector - ComB
4170 |  | Bridging Mode Selector - Com1
4171 |  | Bridging Mode Selector - Com2
4172 |  | Bridging Modbus Start Address - ComB
4173 |  | Bridging Modbus Start Address - Com1
4174 |  | Bridging Modbus Start Address - Com2
4175 |  | Bridging Modbus Start Range - ComB
4176 |  | Bridging Modbus Start Range - Com1
4177 |  | Bridging Modbus Start Range - Com2
4178 |  | Pump Controller Flip Flop Overide
4179 |  | C Drive Format Size (G)
4180 |  | Route Slot Selector
4188 |  | FTP TrendLog Days Back
4189 |  | FTP Alarm Journal Include Selector
4190 |  | FTP Evenmt Log Include Selector
4191 |  | POP3 Poll time (M)
4192 |  | Alarming POP3 Poll time (M)
4193 |  | Daily Report Message Hour Selector
4194 |  | Daily Report Enable Selector
4195 |  | Periodic Report Message Hour
4196 |  | Periodic Report Interval Selector
4197 |  | Current Call Group
4198 |  | Status Alert Message Enable Selector
4199 |  | Alarm Retry Counts
4200 |  | Alarm Auto Acknowledge Selectors
4201 |  | External Cellmodem: Old Message Timeout
4202 |  | MQTT Publish Response Timeout (S)
4203 |  | MQTT Publish Retry Counts
4204 |  | Pump Controller Inter Pump HoldOff
10000 |  | IP Address (4 Char)
10002 |  | Gate Address (4 Char)
10004 |  | Subnet Mask (4 Char)
10006 |  | DNS Address
10008 |  | Ethernet Modbus Port
10009 |  | Ethernet SDX Port
10010 |  | TCP Activity TimeOut
10011 |  | HTTP Port
10012 |  | SDX Unit ID
10013 |  | Ethernet Modbus / DF1 Address
10014 |  | Ethernet Comm Watchdog Timeout( x 0.1 Sec)
10015 |  | Backplane Baud Rate Select
10016 |  | Backplane Parity (0=None, 1 = Even, 2 = Odd)
10017 |  | Backplane Rx Character Gap Extra (x 307uS)
10018 |  | Backplane Xmit En Delay (0.001 S)
10019 |  | Backplane Modbus / DF1 Address
10020 |  | Backplane Str/Fwd In Base Add
10021 |  | Backplane Str/Fwd Out Base Add
10022 |  | Backplane Str/Fwd Add Range
10023 |  | Backplane Comm Watchdog Timeout( x 0.1 Sec)
10024 |  | Backplane Mode Selector
10025 |  | Com1 Baud Rate Select
10026 |  | Com1 Parity (0=None, 1 = Even, 2 = Odd)
10027 |  | Com1 Rx Character Gap Extra (x 307uS)
10028 |  | Com1 Xmit En Delay (0.001 S)
10029 |  | Com1 Modbus / DF1 Address
10030 |  | Com1 Str/Fwd In Base Add
10031 |  | Com1 Str/Fwd Out Base Add
10032 |  | Com1 Str/Fwd Add Range
10033 |  | Com1 Comm Watchdog Timeout( x 0.1 Sec)
10034 |  | Com1 Mode Selector
10045 |  | ComB Bridging Port
10046 |  | Com1 Bridging Port
10048 |  | FTP Server Default Port
10050 |  | SMS Alarm Retry Timer
10051 |  | MQTT Publish Poll Rate
10052 |  | SATServer Poll Rate
10056 |  | Temperature Offset Adjustment 1
10057 |  | Temperature Offset Adjustment 2
10058 |  | Temperature Offset Adjustment 3
10059 |  | Temperature Offset Adjustment 4
10065 |  | IOXM Destination Type Info
10097 |  | TimeZone Offset ( Hours x 10)
10102 |  | Last SLOG entry for Attachments
10104 |  | Diagnostics - mS Late count MAX
10105 |  | Diagnostics - keypress counter
10106 |  | Diagnostics - Max ScanTime for MAIN
10107 |  | Diagnostics - TCP Resets Sent ( Socket not found)
10108 |  | Restarts
10109 |  | RTC Month mm (Jan = 1)
10110 |  | RTC Day dd
10111 |  | RTC Year yy ( 2 digit year)
10112 |  | RTC Hours hh
10113 |  | RTC Minutes mm
10114 |  | RTC Seconds ss
10115 |  | RTC milllisecond Offset
10116 |  | SD Card Status
10117 |  | Monitor Selector
10118 |  | RTC Day of Week
10119 |  | Web6 STATUS
10120 |  | Control Register
10121 |  | MAC
10124 |  | Revision Number
10125 |  | LifeBoat Version
10126 |  | Model Number
10127 |  | Bootloader Version
10128 |  | Manufacturer Date
10129 |  | Manufacturer ID [32 Bit]
10131 |  | Configuration
10133 |  | Serial Number [32 Bit]
10135 |  | Calibration - VIN
65001 |  | RTC Month mm (Jan = 1)
65002 |  | RTC Day dd
65003 |  | RTC Year yyyy ( 4 digit year)
65004 |  | RTC Hours hh
65005 |  | RTC Minutes mm
65006 |  | RTC Seconds ss