## ReadOnly Bits
Modulus Com Status ( 1xxxx ) Communication Register List
Modbus Status | DF1/EIP Bank 3 | Description
1 | 1 | Local DI's
33 | 33 | AI Low Alarm Bits
41 | 41 | AI High Alarm Bits
49 | 49 | Com Fail Status
57 | 57 | Destination ComFail (1-32)
89 | 89 | IO Buss Master Destination ComFail (1-32)
121 | 121 | IO Buss Master Redundant ComFail (1-32)
153 | 153 | IO Buss Master Redundant Active (1-32)
185 | 185 | Pump Error (1-3)
188 | 188 | Pump Controller Error
189 | 189 | Programming Severe Error
190 | 190 | Hardware Fault
191 | 191 | Software Fault
192 | 192 | Network Fault
201 | 201 | Local Force Status
205 | 205 | Basic First Scan
206 | 206 | Basic Run Indicator
207 | 207 | FTP Server file received
208 | 208 | Lockout
209 | 209 | Com Master Config Error Flags
217 | 217 | DO Relay State (1-8)
225 | 225 | Alarm Active (per group)
233 | 233 | Alarming
234 | 234 | Log Run Indicator
235 | 235 | Voice System Busy
257 | 257 | Fault Bits

## Bits
Modulus Com Coil ( 0xxxx ) Communication Register List
Modbus Coils | DF1/EIP Bank 13 | Description
1 | 1 | Local DO's
33 | 33 | PI Totalizer Clear
41 | 41 | Backplane Serial Com Stats Clear
42 | 42 | Ethernet Com Stats Clear
43 | 43 | Com1 Com Stats Clear
44 | 44 | Com2 Com Stats Clear
48 | 48 | Delete Cleared Alarms
49 | 49 | Command Triggers (1-16)
101 | 101 | B Registers ( 1 - 504)
605 |  | FTP Logging Trigger
606 |  | Backplane Serial Master Comm Trigger
607 |  | Ethernet Master Comm Trigger
608 |  | Com1 Master Com Trigger
609 |  | Com2 Master Com Trigger
610 |  | MQTT Publish All Trigger
611 |  | Report Trigger
612 |  | Error Stack Clear
613 |  | Comm Event Trigger (1-128)
741 |  | IO Buss Event Trigger (1-128)
2001 |  | Daylight Savings Time Enable
2009 |  | IO Force Enable
2041 |  | IO Comm Fail Enables ( DO & AO)
2057 |  | DI Invert
2081 |  | DI Filter Enable (DI2 - DI15)
2097 |  | Digital Test Mode Enable
2098 |  | Analog Test Mode Enable
2099 |  | Disable WAN HTTP Config Service
2100 |  | Time Master
2101 |  | TFTP Enable
2102 |  | Radio / Com2 Diagnostics Bridge
2103 |  | Allow Unsecured Log GET's
2104 |  | Use DHCP
2105 |  | Allow Unsecured WUI Read Only Access
2106 |  | Disable Config Register Write Protection
2107 |  | Ethernet Auto PowerDown
2108 |  | Use STARTTLS on Port 587 ( Microsoft Servers )
2109 |  | Temp C / F
2110 |  | Enable IOX Alarming Client System
2111 |  | Ethernet: Use HTTP Accelerator
2112 |  | Enable Debug Mode
2113 |  | Display Underscore as Space
2114 |  | Disable Modbus Redirect on IO Buss
2115 |  | Disable Web Redirect on IO Buss
2116 |  | Enable Slow 8 Sec Trending
2119 |  | Ping Disable
2120 |  | Enable IOX Alarming Server System
2121 |  | Attempt Programming Restart on Error
2122 |  | Programming ScanTime WatchDog Disable
2125 |  | Disable 'Full Website' on Mobile
2126 |  | Enable 'Graphic HMI' on Mobile
2127 |  | Enable High Speed Analog's
2128 |  | Link Layer Disable
2129 |  | PID Reverse Acting Channel 1
2130 |  | PID Reverse Acting Channel 2
2131 |  | PID Reverse Acting Channel 3
2132 |  | PID Reverse Acting Channel 4
2133 |  | Enable Both Float & Level Controller on Local Display
2134 |  | Alive Message - Skip if Alarmed in last 24 hours
2135 |  | On Pump Fail Leave Call On
2136 |  | Show / Enable Redundant UPS data
2137 |  | BackPlane Master Use Retries on Probing
2138 |  | Ethernet Master Use Retries on Probing
2139 |  | Serial Com1 Master Use Retries on Probing
2140 |  | Serial Com2 Master Use Retries on Probing
2142 |  | Programming AutoStart
2144 |  | MQTT Use Secure TLS Connection
2145 |  | Log Category Enable 0
2146 |  | Log Category Enable 1
2147 |  | Log Category Enable 2
2148 |  | Log Category Enable 3
2149 |  | Log Category Enable 4
2150 |  | Log Category Enable 5
2151 |  | Log Category Enable 6
2152 |  | Log Category Enable 7
2153 |  | Log Category Enable 8
2154 |  | Log Category Enable 9
2155 |  | Log Category Enable 10
2156 |  | Log Category Enable 11
2157 |  | Log Category Enable 12
2158 |  | Log Category Enable 13
2159 |  | Log Category Enable 14
2160 |  | Log Category Enable 15
2161 |  | FTP Preface file name with unit Name
2162 |  | Allow off Schedule Acks
2163 |  | MQTT Add Units to Published numbers
2164 |  | Add Alarms to Cleared Report
2165 |  | Only except SMS/ Email Messages from Known Contacts
2169 |  | Ethernet FTP Server Enable
2170 |  | Ethernet FTP Server Anonymous Logon allowed
2171 |  | FTP Relay from Server to Client
2172 |  | External CellModem Enable
2176 |  | Report on Cleared Alarms
2177 |  | Disable SDX Redirect on IO Buss
2178 |  | Trending Strip mode enable
2182 |  | Enable Satellite Time Update
2185 |  | Ethernet Port SDX Enable
2186 |  | Ethernet Port Modbus Enable
2187 |  | Ethernet Port EIP Enable
2193 |  | Bus Port SDX Enable
2194 |  | Bus Port Modbus Enable
2195 |  | Bus Port DF1 Enable
2196 |  | Bus Port BrickNet Enabled
2197 |  | Bus Bridging Eterlogic Enable
2201 |  | Com1 Port SDX Enable
2202 |  | Com1 Port Modbus Enable
2203 |  | Com1 Port DF1 Enable
2204 |  | Com1 Port BrickNet Enabled
2205 |  | Com1 Bridging Eterlogic Enable
2209 |  | Com2 Port SDX Enable
2210 |  | Com2 Port Modbus Enable
2211 |  | Com2 Port DF1 Enable
2212 |  | Com2 Port BrickNet Enabled
2213 |  | Com2 Bridging Eterlogic Enable
2217 |  | N Register Retain Enables
2721 |  | B Register Retain Enables
3225 |  | Master Engine Destination Disable
3257 |  | Master Engine Event Polling Enables
3385 |  | IO Buss Master Event Polling Enable
3513 |  | IO Buss Master Engine Destination Enable
3545 |  | UI Scale Clamp Enable
3553 |  | B Register Write Enables
4057 |  | N Register Write Enables
4561 |  | Display Item on WEB B Registers
5065 |  | Display Item on WEB N Registers
5569 |  | Display Item on WEB Command Triggers
5585 |  | Display Item on WEB IO
5633 |  | Display HMI Scan Enable
5665 |  | Display HMI Write Enable
5697 |  | Text HMI Page Enables
5705 |  | Trending Attach Trace to Right Axis 1-64
5769 |  | Alarm Disable Bits - B's
6273 |  | Alarm Disable Bits - DI's
6290 |  | Alarm Disable Bits - Others

## Read Only Integers
Modulus Com Input Registers ( 3xxxx ) Communication Register List
Modbus Input Registers | DF1/EIP Bank 7 | Description
1 | 1 | AI Registers
9 | 9 | Vin
10 | 10 | Vbatt ( if supported )
11 | 11 | Radio RSSI
12 | 12 | Radio RSSI Latched
13 | 13 | External Cell RSSI
16 | 16 | Ultrasonic Reading
17 | 17 | AI Raw Value
21 | 21 | DI Rate
23 | 23 | DI Interval [32 Bit]
27 | 27 | PID Output
31 | 31 | PID Error
37 | 37 | Ethernet Slave TX/RX Packets [ 2 x 16 Bit]
39 | 39 | Backplane Slave TX/RX Packets [ 2 x 16 Bit]
41 | 41 | Com1 Slave TX/RX Packets [ 2 x 16 Bit]
43 | 43 | Com2 Slave TX/RX Packets [ 2 x 16 Bit]
45 | 45 | Master Destination TX/RX Packets [ 2 x 16 Bit] (1-32)
109 | 109 | IO Buss Master Destination TX/RX Packets [ 2 x 16 Bit] (1-32)
173 | 173 | Master Success - Backplane %
174 | 174 | Master Success - Ethernet %
175 | 175 | Master Success -Com1 %
176 | 176 | Master Success - Com2 %
177 | 177 | Last Source Address - Ethernet
178 | 178 | Last Source Address - Backplane
179 | 179 | Last Source Address - Com1
180 | 180 | Last Source Address - Com2
181 | 181 | Last Destination Address - Ethernet
182 | 182 | Last Destination Address - Backplane
183 | 183 | Last Destination Address - Com1
184 | 184 | Last Destination Address - Com2
185 | 185 | Ethernet Com Fail Counts
186 | 186 | Backplane Com Fail Counts
187 | 187 | Com1 Com Fail Counts
188 | 188 | Com2 Com Fail Counts
189 | 189 | Latency Last - Ethernet
190 | 190 | Latency Last - Backplane
191 | 191 | Latency Last - Com1
192 | 192 | Latency Last - Com2
193 | 193 | Latency Max - Ethernet
194 | 194 | Latency Max - Backplane
195 | 195 | Latency Max - Com1
196 | 196 | Latency Max - Com2
197 | 197 | Destination Com Fail Counts (1-32)
229 | 229 | Destination Latency Last (1-32)
261 | 261 | IO Buss Master Destination Com Fail Counts (1-32)
293 | 293 | Latency Live - Ethernet
294 | 294 | Latency Live - Backplane
295 | 295 | Latency Live - Com1
296 | 296 | Latency Live - Com2
301 | 301 | Last System Code
306 | 306 | Last System Extension
311 | 311 | Error Stack Pointer
312 | 312 | Backplane Com UART Errors
313 | 313 | IOX Resets Received
314 | 314 | IOX Hello's Acknowledged
315 | 315 | IOX Accepts per Second
316 | 316 | IOX Tokens Received
317 | 317 | IOX Collisions
318 | 318 | IOX Next Neighbor
319 | 319 | IOX Longest Accept wait (ms)
320 | 320 | IOX Heath
321 | 321 | IOX Checksum Errors
322 | 322 | IOX Slot Status Bits
354 | 354 | LastCallerId
355 | 355 | Pump Controller Sequence ID
382 | 382 | External CellModem SMS Tx Counts
383 | 383 | External CellModem SMS Rx Counts
384 | 384 | Systick [32 bit]
386 | 386 | Programming Scan Time
387 | 387 | Programming Scan Time MAX
388 | 388 | Programming Error Code
389 | 389 | Programming Error Line
390 | 390 | Programming Error Code (clears after reading in programming)
391 | 391 | System Log Stats (% used)
392 | 392 | Event Log Stats (% used)
393 | 393 | Alarm Journal Log Stats (% used)
394 | 394 | PID P Out [32 bit]
402 | 402 | PID I Out [32 bit]
410 | 410 | PID D Out [32 bit]

## Integers
Modulus Com Holding Registers (4xxxx ) Communication Register List
Modbus Holding Registers | DF1/EIP Bank 17 | Description
1 | 1 | AO Registers
5 | 5 | PI Totalizer (1-2 ) [32 Bit]
9 | 9 | Pump Controller Starts (32Bit)
15 | 15 | Pump Controller RunTime (32Bit)
101 | 101 | N Registers (1 - 240)
605 | 605 | Protection Register
606 | 606 | UI Low Setpoint
610 | 610 | UI High Setpoint
614 | 614 | PID P Gain (x 1000)
618 | 618 | PID I Gain (x 1000)
622 | 622 | PID D Gain (x 1000)
626 | 626 | Pump Controller Lead A On Setpoint
627 | 627 | Pump Controller Lead A Off Setpoint
628 | 628 | Pump Controller Lag A On Setpoint
629 | 629 | Pump Controller Lag A Off Setpoint
630 | 630 | Pump Controller Lag2 A On Setpoint
631 | 631 | Pump Controller Lag2 A Off Setpoint
632 | 632 | Pump Controller Lead B On Setpoint
633 | 633 | Pump Controller Lead B Off Setpoint
634 | 634 | Pump Controller Lag B On Setpoint
635 | 635 | Pump Controller Lag B Off Setpoint
636 | 636 | Pump Controller Lag2 B On Setpoint
637 | 637 | Pump Controller Lag2 B Off Setpoint
638 |  | PI Gate Time
639 |  | reserved
640 |  | PI Interval Watchdog
641 |  | IO Force Value
672 |  | IO Comm Fail Values
682 | ` | DO Output Holdoff Time
688 |  | AI IO High (1-32)
692 |  | AI IO Low (1-32)
696 |  | AI Engineering High (1-32)
700 |  | AI Engineering Low (1-32)
704 |  | Master Poll Interval (100ms) - Backplane
705 |  | Master Poll Interval (100ms) - Ethernet
706 |  | Master Poll Interval (100ms) - Com1
707 |  | Master Poll Interval (100ms) - Com2
708 |  | Master Comm Fail Probe Time (S) Backplane
709 |  | Master Comm Fail Probe Time (S) Ethernet
710 |  | Master Comm Fail Probe Time (S) Com1
711 |  | Master Comm Fail Probe Time (S) Com2
716 |  | Master Respose Timeout (0.1 Sec) - Backplane
717 |  | Master Respose Timeout (0.1 Sec) - Ethernet
718 |  | Master Respose Timeout (0.1 Sec) - Com1
719 |  | Master Respose Timeout (0.1 Sec) - Com2
720 |  | Master Quiet Time (ms) - Backplane
721 |  | Master Quiet Time (ms) - Com1
722 |  | Master Quiet Time (ms) - Com2
723 |  | Master Max Latency (1-32)
755 |  | Master Destination Address (1-32)
787 |  | Master Destination Hop 1 (1-32)
819 |  | Master Destination Hop 2 (1-32)
851 |  | Master Message Local Index (1-128)
979 |  | Master Message Remote Index (1-128)
1107 |  | Destination Port Overide (1-32)
1139 |  | Trend Strip Chart Display Minutes
1140 |  | Web Refresh
1141 |  | Local AI Sensor Sleep Time
1142 |  | Local AI Sensor Warmup time
1143 |  | IO Test Speed (x 0.1 Sec)
1144 |  | Comm Buffer Limit
1145 |  | DNS Lookup Holdoff (S)
1146 |  | IO Buss Polling rate
1149 |  | IOX Event Polling Time (10 mS)
1150 |  | IOX Comm Fail Probe Timer
1151 |  | MIB-NET Slice Time (mS)
1152 |  | MIB-NET Discovery Time (100 mS)
1153 |  | MIB-NET Slice TimeOut (mS)
1154 |  | IOX Event Local Index
1282 |  | IOX Event Remote Index
1410 |  | PID Input Span
1414 |  | PID I/D time (x10mS)
1418 |  | PID Output DeadBand ( x100)
1422 |  | PID Duty Cycle (S)
1426 |  | Display HMI Objects
1458 |  | Pump Controller Debouncing
1462 |  | Sensor Power Selector Object
1463 |  | Alarm Output Selector
1464 |  | Ack All Alarms with B Register
1465 |  | PID Input Selector
1469 |  | PID Enable/Hold Selector
1473 |  | PID Setpoint Selector
1477 |  | PID Analog Out Selector
1481 |  | PID Digital PWM Out Selector
1485 |  | Pump Controller Call Output Selectors
1488 |  | Pump Controller Level Source Selector
1490 |  | Pump Controller A/B Selector
1491 |  | Pump Controller ShutOff A Selector
1492 |  | Pump Controller ShutOff B Selector
1493 |  | Pump Controller Auto Input Selectors
1496 |  | Pump Controller Run Input Selectors
1499 |  | Pump Controller Float Input Selectors
1503 |  | Pump Controller Float Failsafe Timer
1504 |  | Pump Controller Fail Shutdown Timer
1505 |  | Pump Controller Pump Failure Timer
1506 |  | Trace Selector (1-63)
1569 |  | SMS ReAlarm timer
1570 |  | Secondary Local HMI Switch Selector
1571 |  | Local HMI Switch Enable
1572 |  | C Drive Purge before days back
1573 |  | Routing Destination Ports
1581 |  | Routing IP Addresses
1597 |  | Routing Listen Ports
1605 |  | PumpController Pump Fail Selectors
1608 |  | Mirrored Modbus N Register Mapping
1609 |  | Mirrored Modbus B Register Mapping
1610 |  | IO Mode Selector
1641 |  | UI Format Selector
1645 |  | N Register Scaling Block Selector (1-504)
2149 |  | Display TimeOut
2150 |  | Programming Lines per Scan
2151 |  | Web Interface Selector
2152 |  | Dynamic DNS Selector / Enable
2153 |  | Text HMI Boolean ON Verbage (1-50)
2203 |  | HMI Boolean OFF Verbage (1-50)
2253 |  | HMI Boolean Color for Verbage (1-16)
2270 |  | Master Mode Retries - Backplane
2271 |  | Master Mode Retries - Ethernet
2272 |  | Master Mode Retries - Com1
2273 |  | Master Mode Retries - Com2
2274 |  | Master Message Destination Selector
2402 |  | Master Message Type
2530 |  | Master Message Block Size
2658 |  | Destination Protocol Selector (1-32)
2690 |  | MIB-NET Max Discovery Slot
2691 |  | IOX Comfail Threshold
2692 |  | Bad Login Limit ( Number of times before lockout)
2693 |  | Bad Login Lockout Time (M)
2694 |  | Daylight Savings Dates
2698 |  | AI Alarming Hysterisis (0 - 25.5%)
2702 |  | UI Averaging Selector
2706 |  | Display HMI Boolean ON Verbage (1-32)
2738 |  | Display HMI Boolean OFF Verbage (1-32)
2770 |  | IOX Event Destination Selector
2898 |  | IOX Event BlockSize
3026 |  | IOX Event Message Type
3154 |  | PI Filters
3156 |  | IOX Redundant Slave Selector
3188 |  | Pump Controller Mode/Enable Selector
3189 |  | Pump Controller Handoff Selectors
3192 |  | Trace - Strip Chart Interval
3193 |  | Trace Graph Display Style Selector
3194 |  | Trace - Color Selector Trace (1-63)
3257 |  | Trace - Style Selector Trace (1-63)
3320 |  | Trace - Group Enables (1-63)
3383 |  | Basic Startup Delay
3384 |  | IOX Relayed Message Timeout (0.1S)
3385 |  | Alarm Ack ALL with DI Selector
3386 |  | Alarm Group Enables- B's
3890 |  | Alarm Group Enables- DI's
3907 |  | Alarm Group Enables- Local Com Fail's
3915 |  | Alarm Group Enables- Destination ComFail's
3947 |  | Alarm Group Enables- IOX Com Fail's
3948 |  | Alarm Group Enables- AI Alarms
3949 |  | Alarm Group Enables - PumpController
3950 |  | Alarm Group Enables - Programming
3951 |  | Alarm Group Enables - Faults
3954 |  | FTP Interval Selector
3955 |  | FTP Start Time Selector
3956 |  | FTP File Mode Selector
3957 |  | FTP TrendLog Resolution Selector
3958 |  | FTP Data Selector
3959 |  | Ethernet Pre-Ping (S) ##.#
3960 |  | Bridging Mode Selector - ComB
3961 |  | Bridging Mode Selector - Com1
3962 |  | Bridging Mode Selector - Com2
3963 |  | Bridging Modbus Start Address - ComB
3964 |  | Bridging Modbus Start Address - Com1
3965 |  | Bridging Modbus Start Address - Com2
3966 |  | Bridging Modbus Start Range - ComB
3967 |  | Bridging Modbus Start Range - Com1
3968 |  | Bridging Modbus Start Range - Com2
3969 |  | Pump Controller Flip Flop Overide
3970 |  | C Drive Format Size (G)
3971 |  | Route Slot Selector
3979 |  | FTP TrendLog Days Back
3980 |  | FTP Alarm Journal Include Selector
3981 |  | FTP Evenmt Log Include Selector
3982 |  | POP3 Poll time (M)
3983 |  | Alarming POP3 Poll time (M)
3984 |  | Daily Report Message Hour Selector
3985 |  | Daily Report Enable Selector
3986 |  | Periodic Report Message Hour
3987 |  | Periodic Report Interval Selector
3988 |  | Current Call Group
3989 |  | Status Alert Message Enable Selector
3990 |  | Alarm Retry Counts
3991 |  | Radio OTA Speed Selector
3992 |  | Alarm Auto Acknowledge Selectors
3993 |  | External Cellmodem: Old Message Timeout
3994 |  | MQTT Publish Response Timeout (S)
3995 |  | MQTT Publish Retry Counts
3996 |  | Pump Controller Inter Pump HoldOff
10000 |  | IP Address (4 Char)
10002 |  | Gate Address (4 Char)
10004 |  | Subnet Mask (4 Char)
10006 |  | DNS Address
10008 |  | Ethernet Modbus Port
10009 |  | Ethernet SDX Port
10010 |  | TCP Activity TimeOut
10011 |  | HTTP Port
10012 |  | SDX Unit ID
10013 |  | Ethernet Modbus / DF1 Address
10014 |  | Ethernet Comm Watchdog Timeout( x 0.1 Sec)
10015 |  | Backplane Baud Rate Select
10016 |  | Backplane Parity (0=None, 1 = Even, 2 = Odd)
10017 |  | Backplane Rx Character Gap Extra (x 307uS)
10018 |  | Backplane Xmit En Delay (0.001 S)
10019 |  | Backplane Modbus / DF1 Address
10020 |  | Backplane Str/Fwd In Base Add
10021 |  | Backplane Str/Fwd Out Base Add
10022 |  | Backplane Str/Fwd Add Range
10023 |  | Backplane Comm Watchdog Timeout( x 0.1 Sec)
10024 |  | Backplane Mode Selector
10025 |  | Com1 Baud Rate Select
10026 |  | Com1 Parity (0=None, 1 = Even, 2 = Odd)
10027 |  | Com1 Rx Character Gap Extra (x 307uS)
10028 |  | Com1 Xmit En Delay (0.001 S)
10029 |  | Com1 Modbus / DF1 Address
10030 |  | Com1 Str/Fwd In Base Add
10031 |  | Com1 Str/Fwd Out Base Add
10032 |  | Com1 Str/Fwd Add Range
10033 |  | Com1 Comm Watchdog Timeout( x 0.1 Sec)
10034 |  | Com1 Mode Selector
10035 |  | Com2 Baud Rate Select
10036 |  | Com2 Parity (0=None, 1 = Even, 2 = Odd)
10037 |  | Com2 Rx Character Gap Extra (x 307uS)
10038 |  | Com2 Xmit En Delay (0.001 S)
10039 |  | Com2 Modbus / DF1 Address
10040 |  | Com2 Str/Fwd In Base Add
10041 |  | Com2 Str/Fwd Out Base Add
10042 |  | Com2 Str/Fwd Add Range
10043 |  | Com2 Comm Watchdog Timeout( x 0.1 Sec)
10044 |  | Com2 Mode Selector
10045 |  | ComB Bridging Port
10046 |  | Com1 Bridging Port
10047 |  | Com2 Bridging Port
10048 |  | FTP Server Default Port
10050 |  | SMS Alarm Retry Timer
10051 |  | MQTT Publish Poll Rate
10052 |  | SATServer Poll Rate
10053 |  | Wiegand Register 32 bit
10065 |  | IOXM Destination Type Info
10097 |  | TimeZone Offset ( Hours x 10)
10098 |  | Temperature Offset Adjustment
10099 |  | Days Count for CSV reports
10102 |  | Last SLOG entry for Attachments
10104 |  | Diagnostics - mS Late count MAX
10105 |  | Diagnostics - keypress counter
10106 |  | Diagnostics - Max ScanTime for MAIN
10107 |  | Diagnostics - TCP Resets Sent ( Socket not found)
10108 |  | Restarts
10109 |  | RTC Month mm (Jan = 1)
10110 |  | RTC Day dd
10111 |  | RTC Year yy ( 2 digit year)
10112 |  | RTC Hours hh
10113 |  | RTC Minutes mm
10114 |  | RTC Seconds ss
10115 |  | RTC milllisecond Offset
10116 |  | SD Card Status
10117 |  | Monitor Selector
10118 |  | RTC Day of Week
10119 |  | Web6 STATUS
10120 |  | Control Register
10121 |  | MAC
10124 |  | Revision Number
10125 |  | LifeBoat Version
10126 |  | Model Number
10127 |  | Bootloader Version
10128 |  | Manufacturer Date
10129 |  | Manufacturer ID [32 Bit]
10131 |  | Configuration
10132 |  | Software ID
10133 |  | Serial Number [32 Bit]
10135 |  | Calibration - VIN
10136 |  | RTU Board Type
10137 |  | RTU Factory Cal Date
10138 |  | RTU User Cal Date
10139 |  | RTU Serial Number [32 bit]
10141 |  | RTU Manufacturer ID [32 Bit]
65001 |  | RTC Month mm (Jan = 1)
65002 |  | RTC Day dd
65003 |  | RTC Year yyyy ( 4 digit year)
65004 |  | RTC Hours hh
65005 |  | RTC Minutes mm
65006 |  | RTC Seconds ss
Updated 09/08/2021 for Modulus Com Firmware Version 1.04.12