## ICL Application Note 	No. 00010

Upgrading the I/O Processor Binary (BIOS)

This document provided information on how to update the I/O processor binary file using the ScadaBuilder terminal window.  This process is applicable to all Etherlogic controllers as well as all ScadaFelx Plus RTUs.

If you are starting from a new project:

- Connect your computer to the COM1 port on the controller via a null modem serial cable.

- Open ScadaBuilder.

- Click on the “SCADA Bunny”  button.

- Select your working directory and project name.

  - Press OK.

- Select your controller model and option if applicable.

  - Press OK.

- Press the “Open Terminal Emulation Window”  button.

- Back in ScadaBuilder, press the “Stop”  button.

- If you are prompted to do so by ScadaBuilder, press the “Reset” button on the controller.

- At this point you should be at the C:\ prompt in the terminal window.

- Now drag and drop the new elog.hex (or other necessary hex file) into the terminal window.

- This will download the file into the C: directory of the controller.

- Once the download is finished, type bootload elog.hex at the command prompt to run the boot-loader.  (Where “elog.hex” is the file that you downloaded in the step above.)

- Press the “Restart” button to apply the upgrade.

### If you have an existing project:

- Connect your computer to the COM1 port on the controller via a null modem serial cable.

- Open ScadaBuilder.

- Press the “Open Terminal Emulation Window”  button.

- Back in ScadaBuilder, press the “Stop”  button.

- If you are prompted to do so by ScadaBuilder, press the “Reset” button on the controller.

- At this point you should be at the C:\ prompt in the terminal window.

- Now drag and drop the new elog.hex (or other necessary hex file) into the terminal window.

- This will download the file into the C: directory of the controller.

- Once the download is finished, type bootload elog.hex at the command prompt to run the boot-loader.  (Where “elog.hex” is the file that you downloaded in the step above.)

- Press the “Restart” button to apply the upgrade.

### Summary

The above process should allow you to update any .hex file on an Etherlogic controller or ScadaFelx Plus RTU.

Contact Information

Toll Free		(800) 888-1893

Local			(530) 888-1800

Fax			(530) 888-7017

Email			support@iclinks.com

Web			http://www.iclinks.com

Mail			12840 Earhart Avenue ( Auburn, CA USA 95602